## LEONARDO 5.5
LEONARDO 5.5 system
Total thickness: 50 mm
Insulation: Graphite sintered PES (35m)
Plasterboard: Classic and Hydro (15mm)
Pipe diameter: Midix plus 10x1.3mm
Step: 5.5 cm
Weight: 15.7 kg/mq; hydro 16.4 kg/mq
Collector type: SL1
Results
Heating
Active Area | Totale Area | % coverage | Panels 200x120 | Panels 200x60 | Lines number | Collectors number | Max Pressure Loss mbar | Tamb °C | Tm °C | DeltaT °C | Tsup. °C | Q,resa W | Q,tot W | Total heating flow (kg/h) | Water volume (L)
100 | 140 | 71.43% |  |  | 14 | 2 | 300 | 20 | 43 | 3.5 | 33 | 8500 | 9350 | 2297.4541 | 129.081
Cooling
Active Area | Total Area | % coverage | Panels 200x120 | Panels 200x60 | Lines number | Collettors number | Max pressure loss mbar | Tamb °C | Tm °C | DeltaT °C | Tsup. °C | Q,resa W | Q,tot W | Total cooling flow (kg/h) | Water volume (L)
100 | 140 | 71.43% |  |  | 14 | 2 | 300 | 26 | 14 | 2.5 | 22.5741 | 5180 | 5698 | 1960.1338 | 129.081

## LEONARDO 3.5
LEONARDO 3.5 system
Total thickness: 50 mm
Insulation: Graphite sintered PES (35m)
Plasterboard: Classic and Hydro (15mm)
Pipe diameter: Midix plus 10x1,3mm
Step: 3,5 cm
Weight: 15.8 kg/mq; hydro 16.5 kg/mq
Collector type: SL1
Results
Heating
Active Area | Total Area | % coverage | Panels 200x120 | Panels 200x60 | Lines number | Collettors number | Max pressure loss mbar | Tamb °C | Tm °C | DeltaT °C | Tsup. °C | Q,resa W | Q,tot W | Total heating flow (kg/h) | Water volume (L)
100 | 140 | 71.43% |  |  | 14 | 2 | 300 | 20 | 39.5 | 3.5 | 32.9 | 8420 | 9262 | 2275.831 | 157.762
Cooling
Active Area | Total Area | % coverage | Panels 200x120 | Panels 200x60 | Lines number | Collettors number | Max pressure loss mbar | Tamb °C | Tm °C | DeltaT °C | Tsup. °C | Q,resa W | Q,tot W | Total cooling flow (kg/h) | Water volume (L)
100 | 140 | 71.43% |  |  | 14 | 2 | 300 | 26 | 14 | 3 | 21.7143 | 6480 | 7128 | 2043.3827 | 157.762

## LEONARDO 3.0 PLUS
LEONARDO 3.0 PLUS system
Total thickness: 50 mm
Insulation: Graphite sintered PES (40m)
Plasterboard: Active Air Technology (10mm)
Pipe diameter: Midix plus 10x1.3mm
Step: 3 cm
Weight: 15 kg/mq
Collector type: SL1
Results
Heating
Active Area | Total Area | % coverage | Panels 200x120 | Panels 200x60 | Lines number | Collettors number | Max pressure loss mbar | Tamb °C | Tm °C | DeltaT °C | Tsup. °C | Q,resa W | Q,tot W | Total heating flow (kg/h) | Water volume (L)
100 | 140 | 71.43% |  |  | 14 | 2 | 300 | 20 | 37.5 | 3.5 | 32.7 | 8230 | 9053 | 2224.4761 | 175.65
Cooling
Active area | Total Area | % coverage | Panels 200x120 | Panels 200x60 | Lines number | Collettors number | Max pressure loss mbar | Tamb °C | Tm °C | DeltaT °C | Tsup. °C | Q,resa W | Q,tot W | Total cooling flow (kg/h) | Water volume (L)
100 | 140 | 71.43% |  |  | 14 | 2 | 300 | 26 | 14 | 3.5 | 20.6495 | 8090 | 8899 | 2186.6357 | 175.65